This product has received a verified Environmental Product Declaration (EPD) based on a North American Product Category Rule (PCR.)

SECTION 08 42 29.23

SLIDING AUTOMATIC ENTRANCES

Specifier Note: This specification document shall serve as a guide specification for typical projects where the Stanley Access Technologies Dura-Glide GreenStar 2000/3000 Series sliding automatic entrance will be the basis of design. Specification must be reviewed for applicability on a per project basis. Specification is not appropriate for projects where a wind force and/or impact rating are required. The specifier is directed to select appropriate options included herein. Consult with the local Access Technologies Territory Manager, when options, not specified, are required. See last page of this document for a summary of unspecified options.

- GENERAL

  - RELATED DOCUMENTS

    - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

  - SUMMARY

    - This Section includes the following types of automatic entrances:

      - Exterior and interior, single slide and bi-parting, sliding automatic entrances.

    - Related Sections:

      - Division 7 Sections for caulking to the extent not specified in this section.

      - Division 8 Section "Aluminum-Framed Entrances and Storefronts" for entrances furnished and installed separately in Division 8 Section.

      - Division 8 Section "Door Hardware" for hardware to the extent not specified in this Section.

      - Division 8 Section Glazing for materials and installation requirements of glazing for automatic entrances.

      - Division 26 Sections for electrical connections provided separately, including conduit and wiring, for power to sliding automatic entrances.

  - REFERENCES

    - General: Standards listed by reference, including revisions by issuing authority, form a part of this specification section to extent indicated. Standards listed are identified by issuing authority, authority abbreviation, designation number, title or other designation established by issuing authority.  Standards subsequently referenced herein are referred to by issuing authority abbreviation and standard designation.

    - Underwriters Laboratories (UL):

      - UL 325 – Standard for Door, Drapery, Gate, Louver, and Window Operators and Systems.

    - American National Standards Institute (ANSI) / Builders’ Hardware Manufacturers Association (BHMA):

      - ANSI/BHMA A156.10: Standard for Power Operated Pedestrian Doors.

      - ANSI/BHMA A156.5: Standard for Auxiliary Locks and Associated Products

    - American Society for Testing and Materials (ASTM):

      - ASTM B221 - Standard Specification for Aluminum and Aluminum-Alloy Extruded Bars, Rods, Wire, Profiles, and Tubes.

      - ASTM B209 - Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate

      - ASTM E283 - Standard Test Method for Determining Rate of Air Leakage Through Exterior Windows, Curtain Walls, and Doors Under Specified Pressure Differences Across the Specimen.

    - American Association of Automatic Door Manufacturers (AAADM):

    - ASHRAE 90.1: Energy Standard for Buildings Except Low-Rise Residential Buildings.

    - National Fire Protection Association (NFPA):

      - NFPA 101 – Life Safety Code.

      - NFPA 70 – National Electric Code.

    - National Fenestration Rating Council (NRFC).

      - NFRC 100:  Procedure for Determining Fenestration Product U-factors.

      - NFRC 200:  Procedure for Determining Fenestration Product Solar Heat Gain Coefficient and Visible Transmittance at Normal Incidence.

      - NFRC 400: Procedure for Determining Fenestration Product Air Leakage

      - NFRC 500:  Procedure for Determining Fenestration Product Condensation Resistance Values.

    - International Code Council (ICC):

      - IBC: International Building Code

      - IECC: International Energy Conservation Code

    - Building Officials and Code Administrators International (BOCA), 1999:

    - International Organization for Standardization (ISO):

      - ISO 9001 - Quality Management Systems

      - ISO 14025 – Environmental Labels and Declarations -- Type III Environmental Declarations -- Principles and Procedures

      - ISO14040 – Environmental Management -- Life Cycle Assessment -- Principles and Framework

      - ISO 14044 – Environmental Management -- Life Cycle Assessment -- Requirements and Guidelines

      - ISO 21930 – Sustainability in Buildings and Civil Engineering Works -- Core Rules For Environmental Product Declarations Of Construction Products And Services

    - LEED: Leadership in Energy and Environmental Design

    - National Association of Architectural Metal Manufacturers (NAAMM):

      - Metal Finishes Manual for Architectural and Metal Products.

Specifier Note: Modify paragraph below to suit project requirements. - Select appropriate standard finish from options below. - Make multiple selections as required; schedule accordingly. - See last page of this document for a summary of unspecified finish options. - Coordinate with other sections.

    - American Architectural Manufacturers Association (AAMA):

      - [AAMA 606.1 – Integral Color Anodic Finishes for Architectural Aluminum.]

      - [AAMA 607.1 - Clear Anodic Finishes for Architectural Aluminum.]

      - AAMA 611 Voluntary Specification for Anodized Architectural Aluminum.

      - AAMA 701 Voluntary Specification for Pile Weatherstripping and Replaceable Fenestration Weatherseals.

    - United Nations Central Product Classification (UNCPC):

      - UNCPC 4212 - Product Category Rules for Preparing an Environmental Product Declaration for Power-Operated Pedestrian Doors and Revolving Doors

  - DEFINITIONS

    - Activation Device:  Device that, when actuated, sends an electrical signal to the door operator to open the door.

    - Safety Device:  Device that prevents a door from opening or closing, as appropriate.

  - PERFORMANCE REQUIREMENTS

    - General:  Provide automatic entrance door assemblies capable of withstanding loads and thermal movements based on testing manufacturer's standard units in assemblies similar to those indicated for this Project.

    - Operating Range:  Minus 30 deg F (Minus 34 deg C) to 130 deg F (54 deg C).

    - Opening-Force Requirements for Egress Doors: Force shall be adjustable; but, not more than 50 lbf (222 N) required to manually set swinging egress door panel(s) in motion.

    - Closing-Force Requirements:  Not more than 30 lbf (133 N) required to prevent door from closing.

    - Air Infiltration:  Maximum air leakage through fixed glazing and framing areas of 1.0 cfm/sf. (5.1 L/s-m2) of fixed entrance system area when tested according to ASTM E 283 and NFRC 400 at a minimum static-air-pressure difference of 1.57 lbf/sf (75 Pa).

Specifier Note: Modify paragraph below to suit project requirements. The performance of the GreenStar system is directly related to the performance of the selected glass. Performance values below are typical for compliance with local energy codes; however, the size and configuration of the door system specified also impacts performance. With that said, it is incumbent on the specifier to consult with an Access Technologies Professional prior to specifying glazing for the GreenStar system to ensure that performance targets for the installation can be achieved. When energy performance requires validation by a third party, retain reference to work performed by an “NFRC ACE”. Coordinate with other sections.

    - Energy Performance Requirements: Sliding automatic entrances shall be evaluated [, by an NFRC Approved Calculation Entity (ACE), ]to confirm compliance with energy performance requirements as follows:

      - U-Factor: [1.10 – 0.65] BTU/hr-ft2-°F in accordance with NFRC 100.

      - Solar Heat Gain Coefficient (SHGC): [0.25 – 0.64] in accordance with NFRC 200.

      - Visible Light Transmittance (VT): [30 – 60] Percent in accordance with NFRC 200.

      - Condensation Resistance (CR):  [19 – 21] in accordance with NFRC 500.

  - SUBMITTALS

    - General:  Submit the following in accordance with Conditions of the Contract and Division 1 Specification Sections.

    - Shop Drawings:  Include plans, elevations, sections, details, hardware mounting heights, and attachments to other work.

    - Color Samples for selection of factory-applied color finishes.

    - Closeout Submittals:

      - Owner’s Manual.

      - Warranties.

    - Reports:  Based on evaluation performed by a qualified agency, for automatic entrance door assemblies.

      - Environmental Product Declaration.

      - Evaluation Report for compliance with IBC.

    - Informational Submittals:  Manufacturer's product information and applicable sustainability program credits that are available to contribute towards a LEED rated project certification. Credit MR 4.1 and 4.2: Manufacturer's or fabricator's certificate indicating percentage of post-consumer recycled content by weight and pre-consumer recycled content by weight for each Product specified under this Section.

When energy performance requires validation by a third party, retain requirement for “Energy Calculations” performed by an “NFRC ACE”. Coordinate with other sections.

    - [Energy Calculations:  Submit computer simulation data, prepared by an NFRC ACE confirming compliance with energy performance requirements.]

  - QUALITY ASSURANCE

    - Installer Qualifications:  Manufacturer's authorized representative, with certificate issued by AAADM, who is trained for installation and maintenance of units required for this Project.

    - Manufacturer Qualifications:  A qualified manufacturer with a manufacturing facility compliant with under ISO 9001.

    - Manufacturer shall have in place a national service dispatch center providing 24 hours a day, 7 days a week, emergency call back service.

    - Certifications: Automatic sliding door systems shall be certified by the manufacturer to meet performance design criteria in accordance with the following standards:

      - ANSI/BHMA A156.10.

      - NFPA 101.

      - UL 325 listed.

      - IBC.

      - BOCA.

      - ASHRAE 90.1: Air leakage, U-Factor, SHGC, VT, CR.

      - IECC: U-Factor, SHGC, VT, CR.

    - Environmental Product Declaration (EPD): EPD for automatic sliding entrances shall be certified by the manufacturer to comply with the following:

      - Prepared under Product Category Rule (PCR) UNCPC 4212.

      - Conform to ISO standards 14025, 14040, 14044, 21930

      - Life Cycle Assessment Basis: Cradle to Gate, minimum.

    - Source Limitations:  Obtain automatic entrance door assemblies through one source from a single manufacturer.

    - Product Options:  Drawings indicate sizes, profiles, and dimensional requirements of automatic entrance door assemblies and are based on the specific system indicated.  Refer to Division 1 Section "Product Requirements."

    - Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

    - Emergency-Exit Door Requirements:  Comply with requirements of authorities having jurisdiction for automatic entrances serving as a required means of egress.

  - PROJECT CONDITIONS

    - Field Measurements:  General Contractor shall verify openings to receive automatic entrance door assemblies by field measurements before fabrication and indicate measurements on Shop Drawings.

    - Mounting Surfaces: General Contractor shall verify all surfaces to be plumb, straight and secure; substrates to be of proper dimension and material.

    - Other trades:  General Contractor shall advise of any inadequate conditions or equipment.

  - COORDINATION

    - Templates:  Check Shop Drawings of other work to confirm that adequate provisions are made for locating and installing automatic entrances to comply with indicated requirements.

    - Electrical System Roughing-in: Coordinate layout and installation of automatic entrance door assemblies with connections to power supplies.

  - WARRANTY

    - Automatic Entrances shall be free of defects in material and workmanship for a period of one (1) year from the date of substantial completion.

    - During the warranty period the Owner shall engage a factory-trained technician to perform service and affect repairs. A safety inspection shall be performed after each adjustment or repair and a completed inspection form shall be submitted to the Owner.

    - During the warranty period all warranty work, including but not limited to emergency service, shall be performed during normal working hours.

- PRODUCTS

  - AUTOMATIC ENTRANCES

Specifier Note: Modify paragraph below to suit project requirements. - Select 2000 Series for fixed sidelight and/or surface applied entrances. - Select 3000 Series for full breakout entrances

    - Manufacturer: Stanley Access Technologies; Dura-Glide™ GreenStar [2000] [3000] Series sliding automatic entrances.

  - MATERIALS

    - Aluminum:  Alloy and temper recommended by manufacturer for type of use and finish indicated.

      - Headers, stiles, rails, and frames: 6063-T6.

      - Extruded Bars, Rods, Profiles, and Tubes:  ASTM B 221.

      - Sheet and Plate:  ASTM B 209.

    - Sealants and Joint Fillers:  Performed under Division 7 Section "Joint Sealants".

  - AUTOMATIC ENTRANCE DOOR ASSEMBLIES

    - General:  Provide manufacturer's standard automatic entrance door assemblies including doors, sidelights, framing, headers, carrier assemblies, roller tracks, door operators, activation and safety devices, and accessories required for a complete installation.

Specifier Note: Modify paragraph below to suit project requirements. - Select “partial panel” for surface applications. - Select “sliding leaf only” for fixed sidelight applications; including surface applications. - Select appropriate “Mounting”. Coordinate with selections above.

    - Sliding Automatic Entrances:

      - Single Slide Entrances:

        - Configuration: One sliding leaf and one [full sidelight] [partial panel].

        - Traffic Pattern:  Two-way.

        - Emergency Breakaway Capability: [Sliding leaf only] [Sliding leaf and sidelight].

        - Mounting:  [Between jambs] [Surface applied].

      - Bi-Parting Entrances:

        - Configuration: Two sliding leaves and two [full sidelights] [partial panels].

        - Traffic Pattern:  Two-way.

        - Emergency Breakaway Capability: [Sliding leaves only] [Sliding leaves and sidelights].

        - Mounting:  [Between jambs] [Surface applied].

  - COMPONENTS

Specifier Note: Modify paragraph below to suit project requirements. - Select frame size; 4 ½ inch depth is standard.

    - Framing Members:  Manufacturer's standard extruded aluminum reinforced as required to support imposed loads.

      - Nominal Size: [1 3/4 inch by 4 1/2 inch (45 by 115 mm)] [1 3/4 inch by 6 inch (45 by 152 mm)].

      - Concealed Fastening: Framing shall incorporate a concealed fastening pocket, and continuous flush insert cover, extending full length of each framing member.

Specifier Note: Modify paragraph below to suit project requirements. - Select “Stile Design”; “Narrow” is standard. - Select “Bottom Rail Design”; 4 inch is standard. - Select “Muntin Bars”; 2 inch is standard.

    - Stile and Rail Doors and Sidelights:  Manufacturer's standard 1 ¾ inch (45 mm) thick glazed doors with extruded-aluminum tubular stile and rail members. Incorporate concealed tie-rods that span full length of top and bottom rails.

      - Glazing Stops and Gaskets:  Snap-on, extruded-security aluminum stops and preformed gaskets.

      - Stile Design: [Narrow stile; 2 inch (51 mm)] [Medium stile; 3 ½ inch (95 mm)] nominal width.

      - Bottom Rail Design:  Minimum [4 inch (102 mm)] [6 inch (152 mm)] [8 inch (203 mm)] [10 inch (254 mm)] [12 inch (305 mm)] nominal height.

      - Muntin Bars:  [None.] [Horizontal tubular rail member for each door; [2 inch (51 mm)] [4 1/4 inch (108 mm)] nominal width.]

Specifier Note: Modify paragraph below to suit project requirements. The performance of the GreenStar system is directly related to the performance of the selected glass. Performance values below are typical for common, LowE coated, 1 inch (25 mm) insulated glazing units; however, the size and configuration of the door system specified also impacts performance. With that said, it is incumbent on the specifier to consult with an Access Technologies Professional prior to specifying glazing for the GreenStar system to ensure that performance targets for the installation can be achieved.

    - Glazing: Furnished under Division 8 Section Glazing. All Glazing furnished under separate section shall be 1 inch (25 mm) insulated, hermetically sealed, with inboard and outboard glass 1/4 inch (6 mm) tempered.

      - U-Factor Summer Day-Time: [0.27] BTU/hr-ft2-°F (1.56 W/m2-°K)

      - U-Factor Winter Night-Time: [0.29] BTU/hr-ft2-°F (1.68 W/m2-°K)

      - SHGC: [0.12 – 0.40]

      - VT: [15 – 74] Percent

    - Headers:  Fabricated from extruded aluminum and extending full width of automatic entrance door units to conceal door operators, carrier assemblies, and roller tracks.  Provide hinged or removable access panels for service and adjustment of door operators and controls.  Secure panels to prevent unauthorized access.

      - Mounting:  Concealed, with one side of header flush with framing.

      - Capacity: Capable of supporting up to 220 lb (100 kg) per panel, up to four panels, over spans up to 14 feet (4.3 m) without intermediate supports.

    - Carrier Assemblies and Overhead Roller Tracks:  Manufacturer's standard carrier assembly that allows vertical adjustment of at least 1/8 inch (3 mm); consisting of urethane with precision steel lubricated ball-bearing wheels, operating on a continuous roller track. Support panels from carrier assembly by load wheels and anti-riser wheels with factory adjusted cantilever and pivot assembly. Minimum two ball-bearing load wheels and two anti-rise rollers for each active leaf. Minimum load wheel diameter shall be 2 1/2 inch (64 mm); minimum anti-rise roller diameter shall be 2 inch (51 mm).

Specifier Note: Modify paragraph below to suit project requirements. - Select appropriate thresholds for applications. - Make multiple selections as required; schedule accordingly.

    - Thresholds:  Manufacturer's standard thresholds as indicated below:

      - [Continuous standard tapered extrusion square by bevel, with bevel to exterior.]

      - [Continuous standard tapered extrusion square by bevel, with bevel to interior.]

      - [Continuous standard tapered extrusion double bevel.]

      - [Continuous standard square extrusion, for recessed installation.]

      - All thresholds to conform to details and requirements for code compliance.

    - Fasteners and Accessories:  Manufacturer's standard corrosion-resistant, non-staining, non-bleeding fasteners and accessories compatible with adjacent materials.

    - Signage: Provide signage in accordance with ANSI/BHMA A156.10.

  - DOOR OPERATORS

    - General:  Provide door operators of size recommended by manufacturer for door size, weight, and movement; for condition of exposure; and for long-term, operation under normal traffic load for type of occupancy indicated.

    - Electromechanical Operators:  Self-contained overhead unit powered by a minimum of 1/4 horsepower, permanent-magnet DC motor with gear reduction drive, microprocessor controller; and encoder.

      - Operation:  Power opening and power closing.

      - Features:

        - Adjustable opening and closing speeds.

        - Adjustable open check and close check speeds.

        - Adjustable hold-open time between 0 and 30 seconds.

        - Obstruction recycle.

        - On/Off switch to control electric power to operator.

        - Energy conservation switch that reduces door-opening width.

        - Closed loop speed control with active braking and acceleration.

        - Adjustable obstruction recycle time delay.

        - Self-adjusting stop position.

        - Self-adjusting closing compression force.

        - Onboard sensor power supply.

        - Onboard sensor monitoring.

        - Optional Switch to open/Switch to close operation.

        - Fire alarm interface, configurable to safely open or close the entrance on signal from fire alarm system.

      - Mounting:  Concealed.

      - Drive System: Synchronous belt type.

    - Electrical service to door operators shall be provided under Division 26 Electrical.  Minimum service to be 120 VAC, 5 amps.

  - ELECTRICAL CONTROLS

    - Electrical Control System: Electrical control system shall include a microprocessor controller and a high-resolution position encoder. The encoder shall monitor revolutions of the operator shaft and send signals to microprocessor controller to define door position and speed.

      - The high-resolution encoder shall have a resolution of not less than 1024 counts per revolution. Systems utilizing external magnets and magnetic switches are not acceptable.

      - Electrical control system shall include a 24 VDC auxiliary output rated at 1 amp.

    - Performance Data: The microprocessor shall collect, and store performance data as follows:

      - Counter: A non-resettable counter to track operating cycles.

      - Event Reporting: Unit shall include non-volatile event and error recording including number of occurrences of events and errors, and cycle count of most recent events and errors.

      - LED Display: Display presenting the current operating state of the controller.

    - Controller Protection: The microprocessor controller shall incorporate the following features to ensure trouble free operation:

      - Automatic Reset Upon Power Up.

      - Main Fuse Protection.

      - Electronic Surge Protection.

      - Internal Power Supply Protection.

      - Resetable sensor supply fuse protection.

      - Motor Protection, over-current protection.

    - Soft Start/Stop: A “soft-start” “soft-stop” motor driving circuit shall be provided for smooth normal opening and recycling.

    - Obstruction Recycle: Provide system to recycle the sliding panels when an obstruction is encountered during the closing cycle. If an obstruction is detected, the system shall search for that object on the next closing cycle by reducing door closing speed prior to the previously encountered obstruction location, and will continue to close in check speed until doors are fully closed, at which time the doors will reset to normal speed. If obstruction is encountered again, the door will come to a full stop. The doors shall remain stopped until obstruction is removed and operate signal is given, resetting the door to normal operation.

    - Programmable Controller: Microprocessor controller shall be field programmable.

      - The following parameters may be adjusted:

        - Operating speeds and forces as required to meet specified ANSI/BHMA standard.

        - Adjustable and variable features specified.

        - Reduced opening position.

      - Manual programming shall be available through local interface which has a two-digit display with a selection control including three push buttons.

  - ACTIVATION AND SAFETY DEVICES

    - Combined Activation and Safety Sensors: Combined activation and safety sensors shall, in a single housing, detect motion and presence in accordance with ANSI/BHMA A156.10. Motion shall be detected using K-band microwave technology, presence by active infrared reflection technology.

      - Mounting Height: Up to 11.5 feet (3.5 m) above finish floor

      - Temperature Range: Between -31°F and 131°F (-35°C to 55°C) in all environmental conditions

      - Relays: Form C, 50V at 0.3A for both activation and safety.  Hold time of less than 0.5 seconds.

      - Detection Pattern: When detection is made in the activation zone, and the entrance opens, the safety zone shall extend through the threshold on each side; creating an X-pattern. When activation and safety zones are cleared and the entrance closes the sensor will ignore the X-pattern safety zones.

      - Combined motion and presence sensors shall be equal to or better than X-Zone Sensor by Optex.

    - Photoelectric Beams: In addition to the threshold sensor include a minimum of two (2) doorway holding beams.  Photoelectric beams shall be pulsed infrared type, including sender receiver assemblies for recessed mounting.

    - Presence Sensor Monitoring: Sliding automatic entrances control system shall include a means to verify the functionality of all active presence sensors in accordance with ANSI/BHMA A156.10. A detected fault shall cause automatic operation to cease until the fault is corrected.

  - HARDWARE

    - General:  Provide units in sizes and types recommended by automatic entrance door and hardware manufacturers for entrances and uses indicated.

Specifier Note: Paragraphs below describe options for “Emergency Breakaway Feature”, select and edit to suit project requirements. - To include Stanley’s Green-Set-Go feature that will automatically return panels from a breakout event, retain paragraphs 1, 2 and 3. - For standard breakout control include paragraph 4 as noted, and either paragraph 5 or 6. - Paragraph 3: Retain 1st sentence for all; include second sentence when additional control is desired on breakaway sidelights; applicable only to 3000 Series. - Paragraph 5: Limit arms are standard option for panel control on breakout. - Paragraph 6: Wind Dampers provide greater control of panel movement on breakout and are optional to limit arms.

    - Emergency Breakaway Feature:  Provide release hardware that allows panel(s) to swing out in direction of egress to full 90 degrees from any position in sliding mode.  Maximum force to open panel shall be 50 lbf (222 N) according to ANSI/BHMA A156.10.  Interrupt powered operation of panel operator while in breakaway mode.

      - [Emergency breakaway feature shall include at least one magnetic latching device mounted in the top of each breakaway panel to control panel breakaway force.

      - Panel Closer: Provide factory installed concealed hydraulic door closer in each breakaway panel to return panels that have broken out to a fully closed position.

      - Emergency breakaway feature shall be equal to or better than Stanley Access Technologies Green-Set-Go.]

      - [Emergency breakaway feature shall include at least one adjustable detent device mounted in the top of each breakaway panel to control panel breakaway force.] [Additionally, breakaway sidelights shall include a second adjustable detent device mounted in the bottom rail]

      - [Limit Arms: Limit arms shall be provided to control swing of sliding or non-sliding panels on break-out; swing shall not exceed 90 degrees. Limit arms shall be spring loaded to prevent shock, and include adjustable friction damping.]

      - [Wind Resistant Damper: Provide factory installed concealed gas dampers in sliding or non-sliding breakaway panels to protect door panels from wind damage. Dampers shall be designed to slow panel movement after breakout.]

    - Deadlocks:  Manufacturer's standard deadbolt operated by exterior cylinder and interior thumb turn; with minimum 1 inch (25 mm) long throw bolt; ANSI/BHMA A156.5, Grade 1.

      - Cylinders: As specified in Division 8 Section "Door Hardware."

      - Hook Latch: Laminated-steel hook, mortise type, BHMA A156.5, Grade 1.

      - Two-Point Locking: On bi-parting entrances, provide locking system that incorporates a device in the stile of active door leaves that automatically extends a flush bolt into overhead carrier assembly.

    - Control Switch: Provide manufacturer’s standard header mounted rocker switches and door position switch to allow for full control of the automatic entrance door. Controls to include, but are not limited to:

      - One-way traffic

      - Reduced Opening

      - Open/Closed/Automatic

    - Power Switch: Sliding automatic entrances shall be equipped with a two position On/Off rocker switch to control power to the door.

    - Sealing System:  Manufacturer's standard air infiltration control system with replaceable components complying with AAMA 701; made of wool, polypropylene, or nylon woven pile with nylon-fabric or aluminum-strip backing.

      - Meeting Stiles and Stiles Meeting Frames: Slide in type, dual pile.

      - Header/Carrier: Single pile

      - Pivoting Stiles: Pivoting stile seals at threshold.

      - Overlapping Stiles: Dual pile seals.

      - Weather Sweeps: Adjustable dual nylon brush sweeps, concealed in the bottom rail.

      - Air Restriction Blocks: Manufacturer’s standard stile sealing blocks, top and bottom of all stiles.

      - Sealing system shall be equal to or better than Stanley Access Technologies GreenFit sealing system.

  - FABRICATION

    - General:  Factory fabricates automatic entrance door assembly components to designs, sizes, and thickness indicated and to comply with indicated standards.

      - Form aluminum shapes before finishing.

      - Use concealed fasteners to greatest extent possible.

        - Where fasteners are subject to loosening or turning out from thermal and structural movements, wind loads, or vibration, use self-locking devices.

        - Reinforce members as required to receive fastener threads.

    - Framing:  Provide automatic entrances as prefabricated assemblies.

      - Fabricate tubular and channel frame assemblies with manufacturer's standard mechanical or welded joints.  Provide sub-frames and reinforcement as required for a complete system to support required loads.

      - Perform fabrication operations in manner that prevents damage to exposed finish surfaces.

      - Form profiles that are sharp, straight, and free of defects or deformations.

      - Prepare components to receive concealed fasteners and anchor and connection devices.

      - Fabricate components with accurately fitted joints with ends coped or mitered to produce hairline joints free of burrs and distortion.

    - Doors:  Factory fabricated and assembled in profiles indicated. Reinforce as required to support imposed loads and for installing hardware.

    - Door Operators:  Factory fabricated and installed in headers, including adjusting and testing.

    - Glazing:  Fabricate framing with minimum glazing edge clearances for thickness and type of glazing indicated.

    - Hardware:  Factory install hardware to the greatest extent possible; remove only as required for final finishing operation and for delivery to and installation at Project site.

  - ALUMINUM FINISHES

    - General: Comply with NAAMM Metal Finishes Manual for Architectural and Metal Products for recommendations for applying and designing finishes. Finish designations prefixed by AA comply with system established by Aluminum Association for designing finishes.

Specifier Note: Modify paragraph below to suit project requirements. - Select appropriate standard finish from options below. - Make multiple selections as required; schedule accordingly. - See last page of this document for a summary of unspecified finish options.

    - [Class II, Clear Anodic Finish: AA-M12C22A31 Mechanical Finish: as fabricated; Chemical Finish: etched, medium matte; Anodic Coating: Architectural Class II, clear coating 0.40 mils minimum complying with AAMA 611-98, and the following:

      - AAMA 607.1

      - Applicator must be fully compliant with all applicable environmental regulations and permits, including wastewater and heavy metal discharge.]

    - [Class I, Color Anodic Finish: AA-M12C22A42/A44 Mechanical Finish: as fabricated; Chemical Finish: etched, medium matte; Anodic Coating: Architectural Class I, integrally colored or electrolytically deposited color coating 0.70 mils minimum complying with AAMA 611-98, and the following:

      - Color: Dark Bronze.

      - AAMA 606.1

      - Applicator must be fully compliant with all applicable environmental regulations and permits, including wastewater and heavy metal discharge.]

- EXECUTION

  - INSPECTION

    - Examine conditions for compliance with requirements for installation tolerances, header support, and other conditions affecting performance of automatic entrances. Proceed with installation only after unsatisfactory conditions have been corrected.

  - INSTALLATION

    - General:  Do not install damaged components.  Fit frame joints to produce joints free of burrs and distortion. Rigidly secure non-movement joints.

    - Entrances:  Install automatic entrances plumb and true in alignment with established lines and grades without warp or rack of framing members and doors.  Anchor securely in place.

      - Install surface-mounted hardware using concealed fasteners to greatest extent possible.

      - Set headers, carrier assemblies, tracks, operating brackets, and guides level and true to location with anchorage for permanent support.

    - Door Operators:  Connect door operators to electrical power distribution system as specified in Division 26 Sections.

    - Glazing: Performed under Division 8 Section "Glazing" in accordance with sliding automatic entrance manufacturer’s instructions.

    - Sealants:  Comply with requirements specified in Division7 Section "Joint Sealants".

  - FIELD QUALITY CONTROL

    - Testing Services:  Factory Trained Installer shall test and inspect each automatic entrance door to determine compliance of installed systems with applicable ANSI standards.

  - ADJUSTING

    - Adjust door operators, controls, and hardware for smooth and safe operation, for tight closure, and complying with requirements in ANSI/BHMA A156.10.

  - CLEANING AND PROTECTION

    - Clean glass and aluminum surfaces promptly after installation.  Remove excess glazing and sealant compounds, dirt, and other substances.  Repair damaged finish to match original finish. Comply with requirements in Division 8 Section “Glazing”, for cleaning and maintaining glass.

END OF SECTION 08 42 29.23

Available options not specified in this document are summarized as follows:

Integral transoms, with optional number and placement of verticals.

Finish options (Standard Options Specified):

Color anodizing options; “Champagne” to “Black”

Multi-coat Fluoropolymer painted finishes.

Cladding.

Locking options (Standard Options Specified):

3-Point Locks

Lock position indicators

Armored strikes

Electric Solenoid Lock (Fail Safe/Fail Secure)

Access Control Locking with surface or recessed panic hardware.

Activation options.

Control switch options including rotary, keyed rotary, and digital control switch.

Alarm Contacts option, allows for remote monitoring of panel status. Consult with your local Stanley Access Technologies professional for sizing when combined with “Green-Set-Go”.

Emergency Power Options.

Uninterruptible Power Supply (UPS); extended operation.

Fly Open Box; One time operation.

Contact your local Stanley Access Technologies representative for more information on specifying the right sliding automatic entrance for your project.

These specifications represent a “sample” door configuration and depict design features that are commonly used. These specifications do not reflect “standard” features and are provided for informational purposes only. Please note that there is no standard “off the shelf” product.  Stanley custom manufactures each product to its customers’ specifications. It is the customer’s responsibility to validate that a particular configuration of Stanley’s products is suitable for a specific application.  All specifications and designs contained herein are subject to change without notice or obligation.